SINGLE-PIECE FIBERGLASS EQUIPMENT SHELTER

- REFERENCE SPECIFICATIONS, CODES, AND STANDARDS

  - ASTM D256 – Standard Test Methods for Determining the Izod Pendulum Impact Resistance of Plastics.

  - ASTM D638 – Standard Test Method for Tensile Properties of Plastics.

  - ASTM D790 – Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials.

  - ASTM D2583 – Standard Test Method for Indentation Hardness of Rigid Plastics by Means of a Barcol Impressor.

  - All references shall be of the latest revision.

- SUBMITTALS

  - Units

    - All submittals, specifications, drawings, brochures, installation instructions, descriptive literature, etc. shall have all units of measurement in both Imperial and SI units.

  - Drawings

    - Project specific drawings, showing:

      - Critical dimensions.

      - Joints, connections, fasteners.

      - Sizes, spacing, and locations of structural members.

      - Materials and thicknesses of construction.

    - Generic layouts or check marked brochures shall be rejected without review.

  - Specifications

    - Project specific specifications.

    - Generic or check marked specifications shall be rejected without review.

  - Receiving, Handling, and Storage Instructions

  - Installation Instructions

  - Product Warranty

  - Test Data

    - Independent certified test results confirming material properties.

      - Test results are to be performed on specimens representative of the resins and reinforcements submitted upon with such resins and reinforcements listed by the certifying party.

      - Data shall be no more than three (3) years old.

  - Laminate Sample

    - 6-inch [15.24 cm] square sample of representative laminate, upon request.

- RECEIVING, HANDLING, AND STORAGE

  - Receiving

    - Inspect for damage

      - All parts should be inspected upon delivery to the site, noting any missing items or visible damage.

      - Verify that surfaces have not been damaged or otherwise marked during transit.

      - Base and panel connection flanges should also be inspected.

      - For smaller boxed items make sure to verify that all packaging seals are in place and that there is no visible damage to the packaging.

    - Investigate for order correctness and count

      - Once the order has been received review the packing list against what has been received.  Should any items not appear to be present or the configuration of the items does not match the description on the packing list, contact Openchannelflow immediately.

      - Small connection hardware (nuts, bolts, etc.) not attached to the Equipment Shelter ship in individual boxes – with those contents clearly marked.  Special care should be taken to secure these and any other small items that can be misplaced on a job site.

  - Handling

    - While rugged and designed for a long service life, Equipment Shelters must be handled with care.

    - When cranes, hoists, and other machinery are used to Equipment Shelters, spreader bars and lifting straps should always be used.  When performing any overhead lift, all lifting eyes must be used in conjunction with good rigging practices.  Rigging and lifting sequences and schedules of equipment are solely the responsibility of the installing party.

    - Chains, ropes, and the like should never be used to move or position any Equipment Shelters as they may serrate the fiberglass laminate or compromise the protective gel coat surfaces.

    - Lifting eyes are provided at each end (minimum) of Equipment Shelters and may be supplied along the length of the shelter as needed.  All provided lifting eyes must be used to equalize the lifting loads.

  - Storage

    - Equipment Shelters not intended for immediate installation may be stored until the site is ready for their installation.

    - Equipment Shelters should only be stored in a location that is clean, level, and protected from construction traffic.

    - When shipped on pallets, Equipment Shelters should be left on those pallets until such time as they are needed.

- MANUFACTURER

  - Supply Fiberglass Equipment Shelters as manufactured by:

    - Openchannelflow (phone:  855.481.1118 / fax:  855.3316475 / www.openchannelflow.com)

      - Locally represented by:

        - XX

- SUBSTITUTIONS

  - Manufacturers wishing consideration as acceptable substitutes must follow the steps outlined below.

  - Include a copy of this specification section with all applicable plans sheets / details, addendum updates, and all referenced / applicable sections.

  - Each paragraph must be check marked to indicate complete compliance with the specification or clearly marked to indicate a request for deviation from the specification requirements.

    - Use check marks (✔) to denote full compliance with a paragraph as a whole.  If deviations from the specifications are indicated and, therefore requested, underline each deviation and denote by a number in the margin to the right of the identified paragraph.

    - The remaining portions of the paragraph not underlined will signify compliance on the part of the Manufacturer with the specifications.

    - Include a detailed, written justification for each numbered deviation.

    - Failure to comply with the above is sufficient cause to summarily reject the entire request for substitution.

  - Requests for substitution must be made in writing and be received by the engineer’s office a minimum of ten (10) business days before the bid opening.

  - Manufacturers not pre-approved shall not be given consideration.

  - To ensure strict quality control, the Manufacturer may incorporate raw materials from outside vendors, but the Manufacturer must fabricate the final product.

    - Job shopping or outside fabrication / sourcing shall not be acceptable.

  - In addition, the request for substitution must provide information regarding a minimum of ten (10) comparable North American installations, including:

    - Owner’s name, location, and contact information.

    - Application and performance specifications.

    - Date of installation.

    - Operational history.

    - Equipment arrangement, including configuration and materials of construction.

- WARRANTY

  - Equipment Shelters within the continental United States shall be warranted to be free of defects in workmanship and materials for five (5) years with a completed warranty registration.

  - Equipment Shelters outside of the continental United States shall be warranted to be free of defects in workmanship and materials in accordance with the time frame agreed upon.  Warranty work for such locations shall be performed at a location of Openchannelflow’s choosing.

  - The warranty period shall begin from the date of shipment.

- SYSTEM DESCRIPTION

  - Configuration

    - Size:

      - Width:

        - 4-feet 0-inches [1.22 m].

        - 6-feet 0-inches [1.83 m].

        - 8-feet 0-inches [2.44 m].

        - 10-feet 0-inches [3.05 m].

      - Length:

        - __________-feet __________-inches [__________ m].

      - Height (as measured at the highest point of the Shelter):

        - 7-feet 6-inches [2.29 m].

  - Materials of Construction

    - Fiberglass reinforced plastic laminate

      - ISO certified polyester laminating resin:

        - Low VOC.

        - Properties shall meet or exceed:

          - Tensile Strength (ASTM D638)		12,000 psi [82.74 MPa].

          - Flexural Strength (ASTM D790)		23,000 psi [158.6 MPa].

          - Flexural Modulus (ASTM D790)		800,000 psi [5.516 GPa].

          - Barcol Hardness (ASTM D2583)		30.

          - Notched Izod (ASTM D256)		8 ft-lb/in [4.272 J/cm].

          - Temperature limit			150° F [65.56° C].

      - E-glass:

        - Minimum of 30% of laminate content by weight.

        - Silane coupling agent.

        - C-glass shall not be allowed.

    - Gel coat:

      - All surfaces must be gel coated.

      - 15 mil cured thickness.

      - U.V. inhibitors in all gel coat formulations, regardless of application or installation location.

      - Color:

        - Interior surfaces:  	Arctic White.

        - Exterior surfaces:  	Arctic White.

    - Insulating core:

      - Rigid, unfaced, CFC / HCFC free, closed cell polyisocyanurate

        - Properties shall meet or exceed:

          - Density (ASTM D1622)			2.0 lb/ft3 [32 kg/m3]

          - Initial R-value (ASTM C518)		6.0 Hr ft2ºF/Btu [1.06 m2ºC/W]

          - Compressive Strength (ASTM D1621)	27 psi [186 kPa]

          - Shear Strength (ASTM C273)		22 psi [151 kPa]

          - Tensile Strength (ASTM 1623)		41 psi [283 kPa]

          - Surface Burn (E84)

            - Flame spread 			<25

            - Smoke developed			<185

  - Design

    - ASCE 7-05

      - Category	I

      - Wind

        - Speed	135 mph [217.2 kph], basic 3-second

        - Iv		1.15

        - Exposure	C

      - Snow

        - Live Load	45 psf [2.155 kPa]

    - IBC

      - Construction		Type III

      - Occupational group	U

  - Construction

    - Molded construction utilizing X-Web technology.

    - Laminate Schedule:

      - Exterior gel coat:

        - 15 mils cured.

      - Outer laminate:

        - 1/8-inch [0.3175 cm] thick.

      - Insulating core:

        - 2-inch [5.08 cm] thick.

      - Inner laminate:

        - 1/8-inch [0.3175 cm] thick.

      - Inner gel coat:

        - 15 mil cured.

- COMPONENTS

  - Doors

    - Quantity

      - _____ 3068 single door.

      - _____ 3468 single door.

      - _____ 4068 single door.

      - _____ 6068 double door.

      - _____ 6868 double door.

      - _____ 8068 double door.

    - Handedness

      - Outswing.

      - Left handed (LH) (outward opening, hinged on left).

      - Right handed (RH) (outward opening, hinged on right).

    - Door thickness shall be 1 3/4-inches [4.445 cm]

    - Overhead door closer

      - Aluminum finish.

      - ANSI A156.4 Grade 1.

      - ADA compliant / UL listed.

      - Commercial rated.

    - Doors shall be mounted with T-304 stainless steel surface mounted strap hinges.

      - The use of continuous piano hinges or other fastening methods shall not be allowed.

    - EDPM edge-grip door seals shall be applied along the full perimeter of the door opening.

      - Edge-grip trim shall be chemically bonded to door opening.

    - Hardware

      - Knob lockset

        - Stainless steel construction.

        - Exterior keylocking (classroom style).

      - Two-point stainless steel door hardware

        - Exterior lever handle.

        - Interior shall be provided with a door override and cushioned handle.

        - Staple for user-supplied padlock.

      - Panic hardware

        - Stainless steel construction.

        - Exterior key locked ball knob.

        - Interior push bar.

    - Integral door threshold 1/2-inch [1.27 cm] high.

  - Lifting

    - Eyes

      - Minimum of (2) removable lifting eyes

        - 3,400 lb [1,542 kg] vertical load limit / eye (minimum).

        - Construction

          - Hot dipped galvanized steel.

          - T-304 stainless steel.

          - T-316 stainless steel.

  - Mounting Flange

    - Integrally molded base-mounting flange.

      - 3-inches [7.62 cm] wide.

      - 1/4-inch [0.635 cm] thick.

- EQUIPMENT

  - Electrical

    - Conduit

      - PVC, schedule 40.

      - PVC, schedule 80.

      - PVC coated galvanized steel.

      - Galvanized steel.

    - Load Center

        - Plug-in style breakers.

        - Style

          - _____ A main lug, convertible.

          - _____ A main circuit breaker (MCB).

        - NEMA

          - 1 metallic.

          - 3R metallic.

        - Phase

          - Single phase.

          - Three phase.

        - Square D QO11224L125GC.

        - Specialty

          - 125 A main lug.

          - 8 space.

          - NEMA 3R thermoplastic

          - Single phase.

          - GE TPL412R.

    - Outlet

      - Interior.

      - 20 A GFCI.

      - Commercial grade duplex.

      - Clear weather cover.

    - Switch

      - Exterior.

      - Duplex.

        - Independent control of interior lights and fan.

    - Wiring

      - Stranded 12 gauge THHN.

  - HVAC

    - Fan

      - 585 CFM [0.46 CMM].

      - Exhaust.

      - Fiberglass hood with fixed fiberglass insect screen.

    - Heater

      - 1,500 watt.

      - Shallow wall mount frame.

      - Line powered.

      - Integral thermostat.

    - Shutter

      - 10-inch x 10-inch [25.4 cm x 25.4 cm].

      - Intake.

      - Fiberglass hood with fixed fiberglass insect screen.

  - Lighting

    - Control

      - Exterior duplex switch box.

        - Independent control of interior light and fan.

    - Fixture

      - LED.

      - 70 watt (7,100 lumens).

      - Multi-volt (120-277 VAC, 60 Hz) ballast.

      - Wet location, IP65.

  - Mounting

    - (2) 48-inch [121.9 cm] L slotted fiberglass mounting struts (for use with user-supplied mounting panel).

    - Full width x full height encapsulated 3/4-inch [1.905 cm] thick plywood mounted panel as shown on Sheet(s).

- EXECUTION

  - Examination

    - Verify that the Equipment Shelter dimensions are correct and that the site conditions are suitable for installing the unit.

    - Equipment Shelters must remain sealed between the section joints. Where required, apply one or two continuous beads of silicone on all exterior section joints before proceeding with the installation.

  - Installation

    - Concrete Foundation Slab

      - Provide a concrete foundation slab on which to mount / secure the Equipment Shelter.  The slab should extend a minimum of 6-inches [15.24 cm] on all sides beyond the Equipment Shelter and the base mounting flange (if external).

      - The thickness of the slab should be a minimum of 6-inches [15.24 cm], but as local soil conditions may vary, the final design of the slab and anchoring details are the responsibility of the installing party and must be sized so as to prevent wind uplift and any other applicable local conditions.

      - The slab must have a smooth, troweled surface to provide uniform support over the entire base structure.  The slab must be level in both directions to within 1/8-inch [0.3175 cm] and free from exposed aggregate and debris.

    - Lifting the Equipment Shelter

      - Inspect all of the lifting lugs to verify that they are tightly secured to the Shelter sections.

      - Inspect the installation location and surrounding areas for any obstacles (INCLUDING OVERHEAD) that may cause difficulties or present a hazard – addressing them as necessary before proceeding.

      - On the concrete foundation slab caulk out the corners of the intended location of the Equipment Shelter, making sure the installation is square.

      - Using ALL of the provided lifting lugs and PROPER RIGGING TECHNIQUES, move the Equipment Shelter to the desired installation location.

      - If the installation location is suitable and the installation square, lift the Equipment Shelter so that the provided base mounting flange sealant can be applied.

      - Apply the sealant and then lower the Equipment Shelter onto the slab.

    - Securing the Equipment Shelter

      - With all doors shut, drill the concrete foundation slab at each pre-drilled base mounting flange location to the size / depth as indicated by the anchor bolt manufacturer.

      - During initial setting of the Equipment Shelter, anchor bolt locations may be skipped to minimize the time needed to square the Equipment Shelter on the slab.

      - Verify the operation of the door(s).

      - Once the Equipment Shelter has been squared on the slab, the initial anchor bolts should be securely tightened.

      - With the initial anchor bolts secured, the remaining anchor bolts should be installed and secured.

      - Verify the operation of the door(s).

      - All anchor bolt locations should be used to ensure that wind uplift cannot occur.

  - Adjust and Clean

    - Verify that the complete installation meets the criteria above and any additional criteria supplied by the Engineer.

    - Clean surfaces in accordance with the manufacturer’s operation and maintenance instructions.

    - Remove all trash and debris, leaving the site in a clean condition.