MODULAR FIBERGLASS EQUIPMENT SHELTER

- REFERENCE SPECIFICATIONS, CODES, AND STANDARDS

  - ASTM D256 – Standard Test Methods for Determining the Izod Pendulum Impact Resistance of Plastics.

  - ASTM D638 – Standard Test Method for Tensile Properties of Plastics.

  - ASTM D790 – Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials.

  - ASTM D2583 – Standard Test Method for Indentation Hardness of Rigid Plastics by Means of a Barcol Impressor.

  - All references shall be of the latest revision.

- SUBMITTALS

  - Units

    - All submittals, specifications, drawings, brochures, installation instructions, descriptive literature, etc. shall have all units of measurement in both Imperial and SI units.

  - Drawings

    - Project specific drawings, showing:

      - Critical dimensions.

      - Joints, connections, fasteners.

      - Sizes, spacing, and locations of structural members.

      - Materials and thicknesses of construction.

    - Generic layouts or check marked brochures shall be rejected without review.

  - Specifications

    - Project specific specifications.

    - Generic or check marked specifications shall be rejected without review.

  - Receiving, Handling, and Storage Instructions

  - Installation Instructions

  - Product Warranty

  - Laminate Sample

    - 6-inch [15.24 cm] square sample of representative laminate, upon request.

- MANUFACTURER

  - Supply Fiberglass Equipment Shelters as manufactured by:

    - Openchannelflow (phone:  855.481.1118 / fax:  855.3316475 / www.openchannelflow.com)

      - Locally represented by:

        - XX

- SUBSTITUTIONS

  - Manufacturers wishing consideration as acceptable substitutes must follow the steps outlined below.

  - Include a copy of this specification section with all applicable plans sheets / details, addendum updates, and all referenced / applicable sections.

  - Each paragraph must be check marked to indicate complete compliance with the specification or clearly marked to indicate a request for deviation from the specification requirements.

    - Use check marks (✔) to denote full compliance with a paragraph as a whole.  If deviations from the specifications are indicated and, therefore requested, underline each deviation and denote by a number in the margin to the right of the identified paragraph.

    - The remaining portions of the paragraph not underlined will signify compliance on the part of the Manufacturer with the specifications.

    - Include a detailed, written justification for each numbered deviation.

    - Failure to comply with the above is sufficient cause to summarily reject the entire request for substitution.

  - Requests for substitution must be made in writing and be received by the engineer’s office a minimum of ten (10) business days before the bid opening.

  - Manufacturers not pre-approved shall not be given consideration.

  - To ensure strict quality control, the Manufacturer may incorporate raw materials from outside vendors, but the Manufacturer must fabricate the final product.

    - Job shopping or outside fabrication / sourcing shall not be acceptable.

  - In addition, the request for substitution must provide information regarding a minimum of ten (10) comparable North American installations, including:

    - Owner’s name, location, and contact information.

    - Application and performance specifications.

    - Date of installation.

    - Operational history.

    - Equipment arrangement, including configuration and materials of construction.

- WARRANTY

  - Modular Shelters within the continental United States shall be warranted to be free of defects in workmanship and materials for five (5) years with a completed warranty registration.

  - Components carry their own manufacturers’ warranties.

  - Any seals or penetrations must be maintained by the Customer to ensure proper sealing.  The suggested interval is every (2) years. Failure to maintain seals or penetrations may limit or void the warranty.

  - The warranty period shall begin from the date of shipment.

- DESIGN CRITERIA

  - Configuration

    - Size:

      - Width:

        - 4-feet 0-inches [1.22 m].

        - 5-feet 0-inches [1.52 m].

        - 6-feet 0-inches [1.83 m].

        - 7-feet 0-inches [2.13 m].

        - 8-feet 0-inches [2.44 m].

        - 10-feet 0-inches [3.05 m].

        - 12-feet 0-inches [3.66 m].

        - 14-feet 0-inches [4.27 m].

        - 16-feet 0-inches [4.88 m].

      - Length:

        - 6-feet 0-inches [1.83 m].

        - 8-feet 0-inches [2.44 m].

        - 10-feet 0-inches [3.05 m].

        - 12-feet 0-inches [3.66 m].

        - 14-feet 0-inches [4.27 m].

        - 16-feet 0-inches [4.88 m].

        - Consult manufacturer for other sizes/configurations.

      - Height (sidewall):

        - 7-feet 0-inches [2.13 m].

        - 8-feet 0-inches [2.44 m].

          - OPTIONAL :

            - 10-feet 0-inches [3.05 m].

    - Roof:

      - Wind-resistant “hip” design sloping up from all four sides.

        - OPTIONAL:

          - Flat roof design sloping up from all four sides.

      - The roof shall form a permanent weather-proof connection using low-maintenance silicone caulk and U.V. stable seam tape.

      - The roof shall not overhang the walls in order to maximize the shelter’s wind speed rating.

    - Assembly

      - Factory assembled.

        - OPTIONAL:

          - Panel construction for field assembly / disassembly.

  - Materials of Construction

    - Fiberglass reinforced plastic laminate

      - ISO certified polyester laminating resin:

        - Low VOC.

        - Properties shall meet or exceed:

          - Tensile Strength (ASTM D638)		16,000 psi [117.2 MPa].

          - Flexural Strength (ASTM D790)		27,000 psi [186.1 MPa].

          - Flexural Modulus (ASTM D790)		1,200,000 psi [8.273 GPa].

          - Barcol Hardness (ASTM D2583)		30.

          - Notched Izod (ASTM D256)		8 ft-lb/in [4.272 J/cm].

          - Temperature limit			150° F [65.56° C].

        - Orthophthalic resins shall not be allowed.

      - E-glass:

        - Minimum of 30% of laminate content by weight.

    - Gel coat:

      - ISO/NPG formulation.

      - All surfaces must be gel coated.

      - 15 mil cured thickness.

      - U.V. inhibitors in all gel coat formulations, regardless of application or installation location.

      - Colors:

        - Interior surfaces:  	White, to maximize interior illumination.

        - Exterior surfaces:  	White.

          - OPTIONAL:

            - _____ RAL.

    - Construction:

      - The roof and walls shall have continuous boxed X-Web laminations no larger than 18-inches [45.27 cm] x 48-inches [121.92 cm] forming a full encapsulation of the insulating core sections and bonding the inner and outer fiberglass laminates to provide structural integrity and prevent delamination of the fiberglass from the core.

      - Roof deck shall have a flame spread of <25 (ASTM E84) / developed smoke of <185 (ASTM E84).

      - Exterior walls shall have a smooth finished simulated tile pattern molded in.

      - Rolled down, sprayed, or orange peel surfaces shall not be acceptable.

  - Laminate Schedule:

    - Exterior gel coat:

      - 15 mils cured.

    - Outer laminate:

      - 1/8-inch [0.3175 cm] thick.

    - Insulating core:

      - 1-inch [2.54 cm] thick.

      - OPTIONAL Enhanced insulating core:

        - 2-inches [5.08 cm] thick.

        - 3-inches [7.62 cm] thick.

    - Center laminate:

      - 1/8-inch [0.3175 cm] thick.

    - Interior Reinforcement:

      - 1/4-inch [0.635 cm] encapsulated plywood on all interior surfaces.

      - OPTIONAL Enhanced interior reinforcement:

        - 1/2-inches [1.27 cm] thick.

        - 3/4-inches [1.905 cm] thick.

    - Inner laminate:

      - 1/8-inch [0.3175 cm] thick.

    - Inner gel coat:

      - 15 mil cured.

- Design

  - Wind

    - Speed	115 mph [185.1 kph].

      - OPTIONAL Wind speed loadings:

          - 125 mph [201.2 kph].

          - 150 mph [241.4 kph].

          - 175 mph [281.6 kph].

  - Snow

    - Live Load	45 psf [2.155 kPa].

      - OPTIONAL Wind speed loadings:

          - 60 psf [2.873 kPa].

          - 75 psf [3.591 kPa].

          - 90 psf [4.309 kPa].

  - ASCE-7

    - Risk Category 	Type III.

- COMPONENTS

  - Doors

    - Quantity

      - _____ 3068 single door(s).

        - OPTIONAL:

          - _____ 4068 single door(s).

      - _____ 6068 double door(s).

        - OPTIONAL:

          - _____ 8068 single door(s).

    - Drip cap

      - T-316 stainless steel construction.

      - Extending 2-inch [5.08 cm] beyond door opening on each side.

    - Overhead door closer

      - Aluminum finish.

        - OPTIONAL:

          - Stainless steel finish.

      - Heavy duty rated.

      - Hold open action.

    - Hardware

      - Lockset

        - Stainless steel construction.

        - Exterior key locking (classroom style) – no alternate.

      - Three-point stainless steel door hardware

        - Exterior lever handle.

        - Interior shall be provided with anti-entrapment door override and cushioned handle.

        - Staple for user-supplied padlock.

      - Panic hardware

        - Stainless steel construction.

        - Exterior key locked.

        - Interior push bar and cushioned pull handle.

    - Hinges

      - Door(s) shall be mounted with stainless steel surface mounted hinges.

        - OPTIONAL:

          - Stainless steel continuous piano hinge(s).

    - Seals

      - EDPM door seals shall be applied along the full perimeter of the door opening.

    - Threshold

      - Low profile molded in threshold.

    - Accessories

      - Sign

        - Chemical hazard sign.

        - Polyethylene construction.

        - 10-inches [25.4 cm] wide x 7-inches [17.78 cm] high.

        - _____ chemical.

      - Window

        - 1/4-inch [0.635 cm] thick UV resistant polycarbonate secured by a two-piece push-on EPDM edge seal.

        - Screwed-on / bolted windows shall not be allowed.

      - Vent

        - Construction

          - Fixed blade.

          - UL 10C spring-loaded fusible link.

        - Material

          - Aluminum.

          - Stainless steel.

        - Size

          - 12-inch [30.48 cm] x 12-inch [30.48 cm].

          - 16-inch [40.64 cm] x 16-inch [40.64 cm].

  - Lifting Points

    - Minimum of (4) 1/2-inch [1.27 cm] stainless steel lifting points shall be provided, at least one per corner.

    - Lifting points shall not be roof mounted for watertightness.

    - Lifting points are not to be used with metal base frames.

  - Mounting Flanges

    - Integrally molded base mounting flange.

      - Minimum 4-inches [10.16 cm] wide.

        - Measured from the interior laminate surface to the end of the flange.

      - 1/4-inch [0.635 cm] thick.

      - Pockets which reduce a wall’s full insulation value shall not be accepted.

      - Contractor shall use bitumen (or equal – by others) roll sealant to provide for a weather-tight seal between the mounting flange and the concrete base.

- EQUIPMENT

  - Electrical

    - Conduit

      - PVC, schedule 40.

      - PVC, schedule 80.

      - EMT.

      - PVC coated galvanized steel.

      - Galvanized steel.

    - Load Center

        - Plug-in style breakers.

        - Style

          - _____ A main lug, convertible.

          - _____ A main circuit breaker (MCB).

        - Phase

          - Single phase.

          - Three phase.

        - NEMA

          - 1 metallic.

          - 3R metallic.

          - 3R thermoplastic (singe phase 125 A main lug configuration only).

    - Outlet

      - Interior.

      - 20 A GFCI.

      - Commercial grade duplex.

      - In-use weather cover.

    - Switches

      - Exterior.

      - Duplex.

        - Independent control of interior light(s) and fan.

    - Wiring

      - Stranded 12 gauge THHN.

  - HVAC

    - Fan

      - 600 CFM [0.47 CMM].

      - Exhaust or supply (specify).

      - Fiberglass hood with fixed fiberglass insect screen.

      - Consult manufacturer for other sizes.

    - Heater

      - 1,500 watt.

      - Wall mount frame.

      - Line powered.

      - Integral thermostat.

      - Consult manufacturer for other sizes.

    - Shutter

      - 10-inch x 10-inch [25.4 cm x 25.4 cm].

      - Intake or exhaust (specify).

      - Fiberglass hood with fixed fiberglass insect screen.

      - Consult manufacturer for other sizes.

  - Lighting

    - Quantity

    - _____ fixtures shall be provided.

      - Fixtures shall provide at least 117 lumens / ft2 [11 lumens / m2] of illumination.

      - Lighting shall be independently controlled by a weather resistant exterior switch box.

    - Shelter light fixtures shall be:

      - LED.

      - Wet location.

      - 48-inch [121.9 cm] L.

      - 6,000 lumen (minimum).