STORM WATER MANHOLES

- REFERENCE SPECIFICATIONS, CODES, AND STANDARDS

  - AASHTO H-20 – Axial Loading.

  - ASTM C581 – Standard Practice for Determining Chemical Resistance of Thermosetting Resins Used in Glass-Fiber-Reinforced Structures Intended for Liquid Service.

  - ASTM D256 – Standard Test Methods for Determining the Izod Pendulum Impact Resistance of Plastics.

  - ASTM D638 – Standard Test Method for Tensile Properties of Plastics.

  - ASTM D785 – Standard Test Method for Rockwell Hardness of Plastics and Electrical Insulating Materials.

  - ASTM D790 – Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials.

  - ASTM D 2563 – Standard Practice for Classifying Visual Defects in Glass-Reinforced Plastic Laminate Parts.

  - ASTM D2583 – Standard Test Method for Indentation Hardness of Rigid Plastic by Means of a Barcol Impressor.

  - ASTM D2584 – Standard Test Method for Ignition Loss of Cured Reinforced Resins.

  - ASTM D3753 – Standard Specification for Glass-Fiber-Reinforced Polyester Manholes and Wetwells.

  - All references shall be of the latest revision.

- SUBMITTALS

  - Units

    - All submittals, specifications, drawings, brochures, installation instructions, descriptive literature, etc. shall have all units of measurement in both Imperial and SI units.

  - Drawings

    - Project specific drawings, showing:

      - Overall structure length, width, and height.

      - Critical elevations.

      - Ladder, top, coupling, and diversion structure orientations.

      - Joints, connections, fasteners.

      - Sizes, spacing, and locations of structural members, ribs, anchoring clips, and dimensional bracing.

      - Materials and thicknesses of construction.

    - Generic layouts or check marked brochures shall be rejected without review.

  - Specifications

    - Project specific specifications.

    - Generic or check marked specifications shall be rejected without review.

  - Receiving, Handling, and Storage Instructions

  - Installation Instructions

  - Operation and Maintenance Instructions

  - Product Warranty and Warranty Registration Form

  - Upon Request

    - Laminate Sample

      - 6-inch [15.24 cm] square samples of representative manhole barrel laminate, upon request.

    - Quality Assurance Data

      - Fabricator’s Certificate of Compliance with fabrication requirements.

      - Qualifications of fabricator’s Quality Assurance Supervisor.

      - Copy of fabricator’s Quality Assurance Program.

      - Quality Assurance Inspection with:

        - Sample of in-production Quality Assurance Inspection report(s).

        - Sample of certificate of post-production Quality Assurance Inspection report(s).

- MANUFACTURER

  - Supply Storm Water Manholes as manufactured by:

    - Openchannelflow (phone:  855.481.1118 / fax:  855.3316475 / www.openchannelflow.com).

      - Locally represented by:

        - XX.

- SUBSTITUTIONS

  - Manufacturers wishing consideration as acceptable substitutes must follow the steps outlined below.

  - Include a copy of this specification section with all applicable plans sheets / details, addendum updates, and all referenced / applicable sections.

  - Each paragraph must be check marked to indicate complete compliance with the specification or clearly marked to indicate a request for deviation from the specification requirements.

    - Use check marks (✔) to denote full compliance with a paragraph as a whole.  If deviations from the specifications are indicated and, therefore requested, underline each deviation and denote by a number in the margin to the right of the identified paragraph.

    - The remaining portions of the paragraph not underlined will signify compliance on the part of the Manufacturer with the specifications.

    - Include a detailed, written justification for each numbered deviation.

    - Failure to comply with the above is sufficient cause to summarily reject the entire request for substitution.

  - Requests for substitution must be made in writing and be received by the engineer’s office a minimum of ten (10) business days before the bid opening.

  - Manufacturers not pre-approved shall not be given consideration.

  - Manufacturers requesting pre-approval must have been regularly engaged in the application, design, and manufacturing of open channel primary devices for at least ten (10) years.

  - To ensure strict quality control, the Manufacturer may incorporate raw materials from outside vendors, but the Manufacturer must fabricate the final product.

    - Job shopping or outside fabrication / sourcing shall not be acceptable.

  - In addition, the request for substitution must provide information regarding a minimum of ten (10) comparable North American installations, including:

    - Owner’s name, location, and contact information.

    - Application and performance specifications.

    - Date of installation.

    - Operational history.

    - Equipment arrangement, including configuration and materials of construction.

- WARRANTY

  - Storm Water Manholes shall be warranted to be free of defects in workmanship and materials for five (5) years with a completed warranty registration.

  - The warranty period shall begin from the date of shipment.

- SYSTEM DESCRIPTION

  - Configuration

    - Storm Water Manholes shall be monolithic, watertight, corrosion resistant units consisting of (as a minimum):  manhole barrel, top, confined space entry warning sign, coupling, ladder, storm water structure (debris basket / coalescing media), platform, end connections, base, and mounting flange.

    - Diameter

      - 60-inches [1.52 m] I.D.

      - 72-inches [1.83 m] I.D.

      - 96-inches [2.44 m] I.D.

      - Inside diameter tolerance:  +/- 1%.

    - Domed Fiberglass Top

        - A full diameter, fully opening reinforced domed fiberglass cover with stainless steel hardware (hinge, padlockable hasp, and cover support gas struts), fiberglass hinge block, and a neoprene sealing gasket applied to the manhole barrel lip.

        - The cover shall be designed and tested to withstand a minimum 1,000 lb. [453.6 kg] static load.

        - For operator safety, the cover support gas strut shall be sized and mounted so that cover opens at any position unless locked.

    - Height

      - The manhole shall be _____-feet _____-inches [_____ m] high as measured from the inlet invert to the surface grade plus 12-inches [30.48 cm].

    - Construction

      - One-piece construction.

    - Storm Water Structures

      - Wet well

        - The Storm Water Manhole shall be sized so that there shall be an area below the inlet pipe invert capable of holding _____ gallons [_____ liters] of screened / treated water.

        - Removal structure

          - Debris removal

            - Small rectangular shaped T-304 stainless steel trash basket with lifting bail, 18-inches [45.72 cm] wide x 8-inches [20.32 cm] deep x 28-inches [71.12 cm] high.

              - T-304 stainless steel angle guides.

              - Perforated T-304 14 gauge screen with Ø2-inch [5.08 cm] holes on 3-inch [7.62 cm] centers.

            - Medium trapezoidal shaped T-304 stainless steel trash basket, 19 1/8-inches [48.58 cm] wide x 10-inches [25.4 cm] deep – base / 20 3/8-inches [51.75 cm] deep – top x 18-inches [45.72 cm] high.

              - T-304 stainless steel axels mounting phenolic wheels.

              - T-304 stainless steel lift point welded to top of basket.

              - Pultruded fiberglass guides bolted and laminated to the manhole barrel.

          - Oil removal

            - (2) racks of removable coalescing media packs.

            - Fabricated from:

              - Polyvinyl chloride (up to 140° F [60° C).

              - High temperature polyvinyl chloride (up to 150° F [65.56° C).

              - Polypropylene (up to 185° F [85° C).

              - Stainless steel (above 185° F [85° C).

            - Sized for flows up to _____ gpm [_____ l/s].

          - Outlet Elbow

            - The outlet pipe shall be elbowed down to trap surface oil and grease.

            - The inlet to the elbow shall be _____-inches [_____ cm] below the outlet invert.

  - Materials of Construction

    - Manhole

      - Fiberglass reinforced plastic laminate composed of:

        - Unsaturated, single lot, isophthalic polyester resin with U.V. inhibitors

        - E-glass reinforcement.

        - Chemically enhanced silica for improved corrosion resistance, strength, and overall performance.

        - Fillers and additives shall be inert to the environment and construction and may be added as required by the specific manufacturing processes to be used to meet the requirements of this standard but may not include calcium carbonate.

        - Wall thickness shall be sufficient to meet or exceed ASTM D3753 and shall be a minimum of 1/2-inch [1.27 cm] thick.

      - Interior

        - Smooth, resin rich, corrosion resistant to minimize sludge build-up.

        - Light tan.

        - Free of exposed fibers, crazing, delamination, blisters larger than Ø1/2-inch [1.27 cm], and wrinkles with a depth of 1/8 inch [0.3175 cm] or greater.

        - Gel coat or paint is not allowed.

      - Exterior

        - 15 mil (cured) gel coat with U.V. inhibitors on all exterior surfaces.

        - Patterned / rolled glass exterior surface with no exposed fibers, sharp projections, or blisters larger than Ø1/2-inch [1.27 cm].

      - Sign

        - A self-adhesive polyester “Confined Space Entry” sign on the manhole interior.

        - Sign to comply with ANSI Z535.2 and OSHA 1910.145.

      - Base

        - The manhole base shall be not less than 1/2-inch [1.27 cm] thick.

      - Mounting flange

        - 4-inch [10.16 cm] wide x 3/4-inch [1.905 cm] thick integrally molded around the circumference of the manhole barrel for anchoring the manhole to the concrete pad.

      - Pad

        - 3/4-inch [1.905 cm] thick expanded polystyrene bead board for placement between the base of the manhole and the concrete slab.

- END CONNECTIONS

      - Inlet

        - _____-inch [_____ cm] pipe stub.

          - Elastomeric polyvinyl chloride coupling with stainless steel bands to connection to _____-inch [_____ cm] O.D. pipe.

          - Eccentric elastomeric polyvinyl chloride coupling with stainless steel bands to connection to _____-inch [_____ cm] pipe to _____-inch [_____ cm] pipe.

        - Raised face _____-inch [_____  cm] adjustable Van Stone flange.

        - ANSI 150 lb. pattern, flat faced flange to connect to _____-inch [_____ cm] flange.

        - Caulking collar with internal Ø_____-inches [_____ cm].

      - Outlet

        - _____-inch [_____ cm] pipe stub.

          - Elastomeric polyvinyl chloride coupling with stainless steel bands to connection to _____-inch [_____ cm] O.D. pipe.

          - Eccentric elastomeric polyvinyl chloride coupling with stainless steel bands to connection to _____-inch [_____ cm] pipe to _____-inch [_____ cm] pipe.

        - Raised face _____-inch [_____  cm] adjustable Van Stone flange.

        - ANSI 150 lb. pattern, flat faced flange to connect to _____-inch [_____ cm] flange.

        - Caulking collar with internal Ø_____-inches [_____ cm].

- MANHOLE ACCESSORIES

  - Customization

    - Custom gel coat color

      - Manhole exterior gel coat color other than standard gray, with U.V. inhibitors, from manufacturer supplied color chart.

        - ___________________________________.

  - Hoist

    - Portable, collapsible, T-304 stainless steel equipment hoist, with:

      - Dutton-Lainson stainless steel gear / brake winch.

      - 500 lb. [226.8 kg] load capacity.

      - 30-feet [0.9144 m] of Ø1/4-inch [0.635 cm] of stainless steel cable.

      - Stainless steel safety hook.

      - Both in-use and storage wall sockets.

      - For domed and aluminum tops only.

  - Equipment Mounting / Access Options

    - Panel

      - 18-inches [45.72 cm] wide x 18-inches [45.72 cm] high fiberglass equipment mounting panel secured to the manhole interior for mounting flow meters, wireless transmission modules, or other small equipment.

    - Shelf

      - 18-inches [45.72 cm] x 12-inches [30.48 cm] deep fiberglass equipment shelf secured to the manhole interior.

  - Ventilation

    - Passive Ø4-inch [10.16 cm] vent

      - Ø4-inch [10.16 cm] duct extending to within 24-inches [60.96 cm] of the manhole platform and secured with T-304 stainless steel pipe brackets.

      - Integral insect screen.

- FIELD ASSISTANCE

  - Qualified factory representative shall provide on-site assistance, consisting of:

    - (___) days of installation observation.

      - Factory representative shall complete a Certification of Installation Observation.

      - Installation observation shall not alleviate installing party from proper installation liability.

    - (___) days of operator training.