METAL TRAPEZOIDAL FLUMES

- REFERENCE SPECIFICATIONS, CODES, AND STANDARDS

  - Trapezoidal Flumes for Open-Channel Flow Measurement, Transactions of the American Society of Engineers, Vol. 3, No. 2, 1960.

  - Water Measurement in Small Irrigation Channels Using Trapezoidal Flumes, Transactions of the American Society of Engineers, Vol. 9, No. 3, 1966.

  - Measuring Water in Small Channels with WSC Flume, Washington Agriculture Experiment Station, Circular 200, 1952.

  - Trapezoidal Flumes for Measuring Flow in Irrigation Channels, USDA-ARS 41-40, March, 1968.

  - All references shall be of the latest revision.

- SUBMITTALS

  - Units

    - All submittals, specifications, drawings, brochures, installation instructions, descriptive literature, etc. shall have all units of measurement in both Imperial and SI units.

  - Drawings

    - Project specific drawings, showing:

      - Critical dimensions.

      - Joints, connections, fasteners.

      - Sizes, spacing, and locations of structural members, ribs, anchoring clips, and dimensional bracing.

      - Materials and thicknesses of construction.

      - Minimum and maximum flow rates.

    - Generic layouts or check marked brochures shall be rejected without review.

  - Specifications

    - Product specific specifications.

    - Generic or check marked specifications shall be rejected without review.

  - Discharge Tables

    - Level-to-flow discharge tables, showing:

      - Flow equations.

      - Submergence transition, where published.

      - Accuracy, where published.

      - Plan view layout showing critical dimensions and primary point of measurement (Ha).

      - Discharge table source.

  - Receiving, Handling, and Storage Instructions

  - Installation Instructions

  - Operation and Maintenance Instructions

  - Product Warranty Registration Form

- MANUFACTURER

  - Supply Trapezoidal flumes as manufactured by:

    - Openchannelflow (phone:  855.481.1118 / fax:  855.3316475 / www.openchannelflow.com)

      - Locally represented by:

        - XX:

- SUBSTITUTIONS

  - Manufacturers wishing consideration as acceptable substitutes must follow the steps outlined below.

  - Include a copy of this specification section with all applicable plans, sheets / details, addendum updates, and all referenced / applicable sections.

  - Each paragraph must be check marked to indicate complete compliance with the specification or clearly marked to indicate a request for deviation from the specification requirements.

    - Use check marks (✔) to denote full compliance with a paragraph as a whole.  If deviations from the specifications are indicated and, therefore requested, underline each deviation and denote by a number in the margin to the right of the identified paragraph.

    - The remaining portions of the paragraph not underlined will signify compliance on the part of the Manufacturer with the specifications.

    - Include a detailed, written justification for each numbered deviation.

    - Failure to comply with the above is sufficient cause too summarily reject the entire request for substitution.

  - Requests for substitution must be made in writing and be received by the engineer’s office a minimum of ten (10) business days before the bid opening.

  - Manufacturers not pre-approved shall not be given consideration.

  - Manufacturers requesting pre-approval must have been regularly engaged in the application, design, and manufacturing of open channel primary devices for at least ten (10) years.

    - Manufacturing alone shall not be deemed sufficient.

    - Submitting party warrants and guarantees that it manufactures the flume, WITHOUT EXCEPTION.

  - In addition, the request for substitution must provide information regarding a minimum of ten (10) comparable North American installations, including:

    - Owner’s name, location, and contact information.

    - Application and performance specifications.

    - Date of installation.

    - Operational history.

    - Equipment arrangement, including configuration and materials of construction.

- WARRANTY

  - Flumes shall be warranted to be free of defects in workmanship and materials for five (5) years from the date of order completion, with a completed warranty registration.

- SYSTEM DESCRIPTION

  - Configuration

    - Single flume

      - Size:

        - _____ Trapezoidal flume.

      - Construction:

        - One-piece construction.

        - Multi-piece construction, with connection hardware.

  - Materials of Construction

    - Aluminum:

      - 1/8-inch [3.175 mm] (as required).

      - 1/4-inch [6.35 mm] (as required).

    - Steel:

      - Galvanized steel.

        - Cold galvanization applied to all welds and sharp bends.

      - Stainless steel:

        - T-304L.

        - T-316L.

      - Gauge thickness:

        - 16 gauge.

        - 12 gauge.

        - 1/4-inch [6.35 mm] (as required).

    - Dimensional bracing:

      - Welded or bolt-on bracing capable of providing sufficient strength and structural support to resist the stresses of shipping and installation (cribbing of the flume is still required during installation).

        - 1-inch x 1-inch [2.54 cm x 2.54 cm] (Small 60 V Trapezoidal flumes).

        - 2-inch x 2-inch [5.08 cm x 5.08 cm] all except flume sizes listed above / below.

        - 3-inch x 3-inch [7.62 cm x 7.62 cm] (8-inch 60, 12-inch 45 SRCRC No. 1, 12-inch 38 SRCRC No. 2).

    - Flanges:

      - Integral top flanges:

        - 2-inches [5.08 cm] wide (minimum).

    - Anchoring clips:

      - Anchor clips on the exterior of the flume to aid in securing the flume during installation.

      - Pre-drilled with Ø5/8-inch [1.59 cm] hole.

      - Quantity and placement as shown on project sheets.

  - Dimensional Tolerances:

    - Flume dimensions shall be plus or minus:

      - 2%.

- ACCESSORIES

  - End Connections

    - Inlet

      - End adapter

        - To transition the flow into the flume, with:

          - _____-inch [_____ cm] pipe stub.

            - Elastomeric polyvinyl chloride coupling with stainless steel bands to connection to _____-inch [_____ cm] O.D. pipe.

          - ANSI 150 lb. pattern, flat faced fiberglass flange to connect to _____-inch [_____ cm] flange.

          - Removable manual bar screen / trash rack for occasional solids screening.

          - Removable energy absorber to break up the velocity profile of energetic incoming pipe flow.

          - Removable set of flow straighteners to break up incoming flow patterns and provide a more uniformly distributed velocity profile.

          - Removable set of perforated polyvinyl chloride plates to provide a more uniformly distributed velocity profile.

    - Outlet

      - End adapter

        - To transition the flow out of the flume, with:

          - _____-inch [_____ cm] pipe stub.

            - Elastomeric polyvinyl chloride coupling with stainless steel bands to connection to _____-inch [_____ cm] O.D. pipe.

          - ANSI 150 lb. pattern, flat faced fiberglass flange to connect to _____-inch [_____ cm] flange.

  - Flow / Level Options

    - Bubbler tube

      - Field removable / replaceable T-316 stainless steel bubbler tube mounted flush to the flume wall and secured through the use of (2) nuts on the top flange of the flume.

      - Compression couplings shall be not allowed.

    - Probe well

      - Vertical 2-inch [5.08 cm] x 3-inch [7.62 cm] rectangular well with Ø2-inch [5.08 cm] opening on the flume sidewall and extending 3-inches [7.62 cm] below the crest (floor) of the flume (for the installation of a pressure transducer probe).

    - Staff / level gauge

      - Surface applied, high visibility, direct read level gauge with 3/4-inch [1.095 cm] black letters / numerals on a reflective white background.

      - Dual scale graduated in centimeter, 1/10-foot, and 1/100-foot increments.

    - Stilling well

      - Attached, with Ø2-inch [5.08 cm] opening in flume sidewall and extending 3-inches [7.62 cm] below the crest (floor) of the flume.

        - 6-inch [15.24 cm].

        - 8-inch [20.32 cm].

        - 12-inch [30.48 cm].

        - 16-inch [40.64 cm].

      - Detached, with Ø2-inch [5.08 cm] coupling in flume sidewall (interconnection tubing by others) and extending 3-inches [7.62 cm] below the crest (floor) of the flume.

        - 6-inch [15.24 cm].

        - 8-inch [20.32 cm].

        - 12-inch [30.48 cm].

        - 16-inch [40.64 cm].

    - Ultrasonic mounting bracket

      - Horizontally and vertically adjustable stainless steel construction.

      - Capable of simultaneously mounting ultrasonic transducers up to Ø1-inch [2.54 cm] NPT and temperature sensors up to Ø1-inch [2.54 cm] NPT.

  - Parameter Monitoring Options

    - Probe well

      - 2-inch [5.08 cm] x 3-inch [7.62 cm] rectangular well with Ø2-inch [5.08 cm] opening on the flume sidewall and extending 3-inches [7.62 cm] below the crest (floor) of the flume (for the installation of a pressure transducer probe).

    - Sampler tube

      - Field removable / replaceable T-316 stainless steel sampler tube mounted flush to the flume wall and secured through the use of (2) nuts on the top flange of the flume.

      - 3/8-inch [9.525 mm] tube to accept standard 3/8-inch [9.525 mm] suction line.

  - Customization

    - Bolt down cover

      - Removable flat bolt down fiberglass cover over flume, with free (non-encapsulated) T-316 stainless steel hardware.  U.V. inhibited gel coat on all cover surfaces.

      - Removable clear, U.V. stable polycarbonate flat cover over flume, with free (non-encapsulated) T-316 stainless steel hardware.

- FIELD ASSISTANCE

  - Qualified factory representative shall provide on-site assistance, consisting of:

    - (___) days of installation observation.

      - Factory representative shall complete a Certification of Installation Observation.

      - Installation observation shall not alleviate installing party from installation liability.

    - (___) days of operator training.